## Slide 1: Fire Pump Controllers 101
SGM Engineering

## Slide 2: Fire Pump Controllers 101
Outline
Codes and Standards
Listing and Approval Agencies
General (electric motor & diesel engine driven fire pump controllers)
Electric Fire Pump Controllers (electric motor driven)
Diesel Fire Pump Controllers (diesel engine driven)
Jockey Pump Controllers

## Slide 3: Fire Pump Controllers 101
Codes & Standards
NFPA – National Fire Protection Association
NFPA 20 – Standard for the Installation of Stationary Pumps for Fire Protection
  Latest Edition 2019
Chapters pertinent to fire pump controllers
    Chapter 10 – Electric
    Chapter 12 - Diesel

## Slide 4: Fire Pump Controllers 101
Codes & Standards
NEC – National Electrical Code
Section 695 – Fire Pumps
Pertinent to electrical installation requirements
Latest Editions 2014
Same as NFPA70

## Slide 5: Fire Pump Controllers 101
Listing & Approval
UL – Underwriters Laboratory
Headquarters in Northbrook, IL
Scope of business is the protection of life and property
Issues “Listings” in regards to equipment built to the NFPA20 standard

## Slide 6: Fire Pump Controllers 101
Listing & Approval
FM Global (aka Factory Mutual)
Headquarters in Boston, MA
Scope of business is the protection of life and property
Issues “Approvals” in regards to equipment built to the NFPA20 standard

## Slide 7: Fire Pump Controllers 101
General
A fire pump controller serves to protect life and property and not the equipment it controls
Devices serving to protect a motor, engine or pump are not allowed per NFPA20, UL and FM
  Ex: overload, low oil pressure, high temperature, low suction pressure

## Slide 8: Fire Pump Controllers 101
General
However, NFPA20, UL and FM do allow the controller to stop the pump under these conditions only:
  Electric Fire Pump Controller
    Locked rotor
  Diesel Fire Pump Controller
    Overspeed

## Slide 9: Fire Pump Controllers 101
General
Location
  Controller shall be located within sight of the fire pump and vice versa
  Controller shall be installed so that all load carrying components are 12” above floor
  Controller shall not be used as a junction box
    Jockey pump shall not be powered by the fire pump controller

## Slide 10: Fire Pump Controllers 101
General
Enclosure NEMA type rating
  Minimum rating as per NFPA20 is type 2
      Drip-proof (water falling from above)

## Slide 11: Fire Pump Controllers 101
General
Pressure sensing assembly
  Pressure transducer
  Test solenoid valve
  1/2 inch connection for sensing line
  3/8 inch drain connection

## Slide 12: Fire Pump Controllers 101
General
Allowable Starting Modes
  Manual start (START pushbutton)
  Automatic start (pressure drop)
  Manual or automatic external device
    Remote start station
    Deluge valve
    Emergency start

## Slide 13: Fire Pump Controllers 101
General
Allowable Stopping Modes
  Manual stop (STOP pushbutton)
  Automatic stop/shutdown (After the expiration of a minimum run timer if starting cause is no longer present
    Note: Automatic stop/shutdown must be approved by AHJ

## Slide 14: Fire Pump Controllers 101
General
Allowable Testing Modes (start and stop)
  Manual “Run Test”
      Will start upon activation of the “Run Test” pushbutton and stop after the expiration of the test duration timer
  Programmed “Periodic Test”
      Will start at a pre-determined adjustable time and date upon activation of the test solenoid valve and stop after the expiration of the test duration timer

## Slide 15: Fire Pump Controllers 101
Electric Fire Pump Controllers
Types
  Full Service
  Limited Service
  Other types*
      Variable Speed
      Medium Voltage
      Residential
*Note: Other types are not supplied with a ViZiTouch V2 Operator Interface.

## Slide 16: Fire Pump Controllers 101
Electric Fire Pump Controllers
Full Service
  UL Listed / FM Approved
  3 phase power only (single phase not allowed)
  No limitation of horsepower (5hp and up)
*Note: Other types are not supplied with a ViZiTouch Operator Interface.

## Slide 17: Fire Pump Controllers
Starting Methods Summary
 | ACROSS- THE-LINE | PART WINDING | AUTO TRANSFORMER | SOFT START SOFT STOP | PRIMARY RESISTOR | WYE-DELTA CLOSED TRANSITION | WYE-DELTA OPEN TRANSITION
MODEL NUMBER | GPA | GPP | GPR | GPS | GPV | GPW | GPY (5)
STARTING VOLTAGE PER WINDING | FULL | FULL | REDUCED | REDUCED | REDUCED | REDUCED | REDUCED
TYPICAL VOLTAGE APPLIED AT MOTOR STARTING (% Vn) | 100% | 100% | 65% | 30% - 50% (adjustable) | 70% | 100% | 100%
PEAK INRUSH CURRENT AT STARTING | (10 - 28) x FLA | (5 - 14) x FLA | (4 - 11) x FLA | NEGLIGIBLE | (7 - 20) x FLA | (3.5 - 9) x FLA | (3.5 - 9) x FLA
PEAK INRUSH CURRENT AT TRANSITION | - | (2 - 5) x FLA | (4 - 11) x FLA | NEGLIGIBLE | (7 - 20) x FLA | NEGLIGIBLE | (3.5 - 9) x FLA
STARTING CURRENT (% FLA) | 500% -1000% | 250% - 500% | 210% - 420% | 250%-450% | 350%-700% | 165% - 330% | 165% - 330%
TRANSITION CURRENT (% FLA) | - | 250% - 500% | 210% - 420% | - | 350% - 700% | 165% - 330% | 165% - 330%
STARTING TORQUE (% FLT) | 50% - 150% | 25% - 75% | 40% - 85% | 10% - 100% (adjustable on Torque Ramp mode) | 50% - 75% | 20% - 50% | 20% - 50%
MOTOR TYPE | STANDARD | 6 WINDINGS | STANDARD | STANDARD | STANDARD | STANDARD WYE-DELTA | STANDARD WYE-DELTA
NUMBER OF WIRE CONNECTIONS | 3 WIRE | 6 WIRE | 3 WIRE | 3 WIRE | 3 WIRE | 6 WIRE | 6 WIRE

## Slide 18: Fire Pump Controllers
Starting Methods: Full Voltage - Across the Line (Direct on Line)

## Slide 19: Fire Pump Controllers
Starting Methods: Reduced Voltage – Electronic Soft Starter
(Soft Start / Soft Stop)

## Slide 20: Fire Pump Controllers
Starting Methods: Reduced Voltage – Wye Delta Open

## Slide 21: Fire Pump Controllers
Starting Methods: Reduced Voltage – Wye Delta Closed

## Slide 22: Fire Pump Controllers
Starting Methods: Reduced Voltage – Wye Delta Closed
Starting Method: Reduced Voltage - Wye-delta closed
Typical Voltage Applied at Start: 100%
Inrush Current: 33% of normal load current
Starting Torque: 33%
Motor Type: Wye-delta
No. of Contactors: 2 at 58%, 1 at 33% of motor full load current (FLC)
Min. ampacity of motor conductors: 6 at 125% x 58% of FLC

## Slide 23: VFD - Benefits
A Variable Speed Controller will:
  Eliminate water surge and hammer in the piping on pump start up
  Reduce current surge on start up of fire pump and reduce generator set sizing
  Save money on installations and maintenance where high pressure piping and fittings are required to handle pump overpressure
  (Can) eliminate the need for floor-by-floor Pressure Control
  (Can) eliminate “Break Tanks” on systems with fluctuating supply pressures
  Save water during weekly testing without draining from the main relief valve
  (Can) increase the number of floors serviced by the fire pump without Pressure Reducing Valves (PRV)
  Be ideally suited for ESFR systems, large campuses, hospital applications, high rise and retrofit for code upgrade purposes

## Slide 24: Shut Off Pressure – Eliminated
Pump shut-off
Pump
Over-pressure
VPx Pump Pressure
Back

## Slide 25: Fire Pump Controllers 101
Electric Fire Pump Controllers
Full Service
  Voltmeter mounted on door front
  Ammeter mounted on door front

## Slide 26: Fire Pump Controllers 101
Electric Fire Pump Controllers
Full Service
  Short Circuit Withstand Rating
    Industry standard: 100,000A
    Optional ratings available
  Across-the-line or reduced voltage start

## Slide 27: Fire Pump Controllers 101
Electric Fire Pump Controllers
Full Service
  Locked rotor protection
    6 x motor full load amperage (FLA, FLC)
    Factory set and calibrated to trip (open) between 8 and 20 seconds
  Emergency start mechanism
    Across the line start even if starting method is reduced voltage

## Slide 28: Fire Pump Controllers 101
Electric Fire Pump Controllers
Full Service
Single operator for ON-OFF

## Slide 29: Fire Pump Controllers 101
Electric Fire Pump Controllers
Full Service
  Visual indications
    Power Available
    Motor RUN
    Phase Reversal

## Slide 30: Fire Pump Controllers 101
Electric Fire Pump Controllers
Full Service
Visual indications
  Automatic or non-automatic
  Type of Actuation
    Pressure or non-pressure
  Type of Shutdown
    Manual or automatic

## Slide 31: Fire Pump Controllers 101
Electric Fire Pump Controllers
Full Service
Contacts for remote alarm annunciation
  Power Available
  Motor RUN
  Phase Reversal

## Slide 32: Fire Pump Controllers 101
4” Alarm Bell
Externally mounted pressure transducer and run test solenoid valve with protective cover.
Key lock
Lifting Lugs
Exterior and Interior USB Port
ViZiTouch V2 Operator Interface
Custom designed IS/CB operator handle
Electric Fire Pump Controllers

## Slide 33: Fire Pump Controllers 101
Electric Fire Pump Controllers
Surge arrestor
I/O board with removable alarm contact terminals
Model GPA
Circuit Breaker & Isolating switch assembly
Motor Contactor
Custom designed emergency start mechanism with integrated limit switch

## Slide 34: Fire Pump Controllers 101
Automatic Power Transfer Switch
Full Service
  Automatic Power Transfer Switch
    Required if normal utility power is not reliable
    Housed in a barriered compartment or in a separate enclosure attached to the fire pump controller

## Slide 35: Fire Pump Controllers 101
Automatic Power Transfer Switch
Full Service
  Automatic Power Transfer Switch
    Listed and Approved for fire pump service
    Transfer switch TEST pushbutton

## Slide 36: Fire Pump Controllers 101
Automatic Power Transfer Switch
Full Service
  Contacts for remote alarm annunciation
    Isolating switch in the OFF position
    Transfer switch in normal position
    Transfer switch in alternate (emergency) position

## Slide 37: Fire Pump Controllers 101
4” Alarm Bell
Externally mounted pressure transducer and run test solenoid valve with protective cover.
Key lock
Exterior and Interior USB Port
Lifting Lugs
ViZiTouch V2 Operator Interface
Custom designed IS/CB operator handle
Automatic Power Transfer Switch

## Slide 38: Fire Pump Controllers 101
Automatic Power Transfer Switch
I/O board with removable alarm
contact terminals
Gland plate
Model GPU
Circuit Breaker & Isolating switch assembly
Surge arrestor
Transfer Switch

## Slide 39: Fire Pump Controllers 101
Electric Fire Pump Controllers
Limited Service
Has all the requirements of a full service fire pump controller except for:
    UL Listed only
    Three phase and single phase power is allowed
    HP rating limited to and including 30hp

## Slide 40: Fire Pump Controllers 101
Electric Fire Pump Controllers
Limited Service
  Use (installation) must be approved by AHJ
  Only across-the-line starting is allowed

## Slide 41: Fire Pump Controllers 101
Diesel Fire Pump Controllers
Operates off of engine batteries
    12VDC or 24VDC
Single phase power required to power the battery chargers
Individual (two) battery chargers
Monitors the battery status and keeps batteries charged and ready to start engine when required

## Slide 42: Fire Pump Controllers 101
Diesel Fire Pump Controllers
HAND-OFF-AUTO selector switch behind a lockable but breakable cover
Individual (two) crank pushbuttons
7 – day pressure recorder

## Slide 43: Fire Pump Controllers 101
Diesel Fire Pump Controllers
Audible alarm

## Slide 44: Fire Pump Controllers 101
Diesel Fire Pump Controllers
Visual indications
  Battery voltage
  Battery amperage
  AC power on
  Main selector switch in automatic position
  Battery 1 and 2 failure
  Engine run
  Charger 1 and 2 failure
  Engine low oil pressure
  Engine high temperature
  Engine overspeed

## Slide 45: Fire Pump Controllers 101
Diesel Fire Pump Controllers
Contacts for remote alarm annunciation
  Engine RUN
  Common controller trouble
  Selector switch in OFF or HAND
  Common engine trouble
  Common pump room alarm

## Slide 46: Fire Pump Controllers 101
Diesel Fire Pump Controllers
Alarm and shutdown schedule
Alarm and shutdown schedule |  | Automatic Start | Manual Start or Remote Start | Run Test or Periodic Test
 | High Coolant | Alarm only | Alarm only | Shutdown
 | Low Oil Pressure | Alarm only | Alarm only | Shutdown
 | Overspeed | Shutdown | Shutdown | Shutdown

## Slide 47: Fire Pump Controllers 101
Diesel Fire Pump Controllers
Externally mounted pressure transducer and run test solenoid valve with protective cover
Hand-Off-Auto selector switch
Key Lock
4” Alarm Bell
ViZiTouch V2
Operator Interface
Exterior USB Port

## Slide 48: Fire Pump Controllers 101
Diesel Fire Pump Controllers
Battery chargers
Automotive type
engine connections
Gland plate
Interior
USB Port
EMI filter
AC and DC isolation circuit breakers
I/O board with removable alarm contact terminals

## Slide 49: Fire Pump Controllers 101
Jockey Pump Controllers
Not considered a “Fire Pump Controller”
Not UL Listed or FM Approved for fire pump service
UL Listed as an Industrial Pump Controller (UL508A)

## Slide 50: Fire Pump Controllers 101
Jockey Pump Controllers
Required to start and stop a pressure maintenance pump (jockey pump) in order to maintain the sprinkler system pressure
Jockey pump shall not be powered by the fire pump controller

## Slide 51: Fire Pump Controllers 101
Jockey Pump Controllers
iPD+ Operator Interface
Digital Display
Type 2 Enclosure
Main Disconnect
Wall Mounting Lugs (4)
2 top – 2 bottom

## Slide 52: Fire Pump Controllers 101
Jockey Pump Controllers
Pressure transducer with 0-600psi range and stainless
steel construction
Fuseless magnetic motor starter with thermo-magnetic motor protector and horsepower rated contactor
Horsepower rated door interlocked rotary type disconnect switch

## Slide 53: Model OPD UL Listed Disconnecting Device
Preface – USA Installations
The installation of a disconnecting means ahead of an electric fire pump controller has always been permitted by NFPA20 and NFPA70 (NEC)
The method of sizing/selecting the disconnecting means device has been for it to hold locked rotor current (6 x FLA) indefinitely (continuously)
In the NFPA20 2013 edition and the NFPA70 2014 edition changes were made to the articles in question

## Slide 54: Model OPD UL Listed Disconnecting Device
Standard Features
Suitable as service entrance equipment
NEMA Type 2 enclosure
Disconnect markings as per
NFPA70 (NEC) 695.4(B)(3)(c)

## Slide 55: Model OPD UL Listed Disconnecting Device
Standard Features
Overcurrent protection device
Flange mounted disconnect handle lockable in the ON (closed) position as per NFPA70 (NEC) 695.4(B)(3)(a)(2)
Grounding lug

## Slide 56: Model OPD UL Listed Disconnecting Device
Typical Installation Schematic

## Slide 57: Thank you!
Tornatech Inc. (Head Office)
Laval, Quebec, Canada Tel: +1 514 334 0523 Toll Free: +1 800 363 8448
Tornatech Europe SPRL
Wavre, Belgium Tel: +32 (0) 10 84 40 01
Tornatech FZE
Dubai, United Arab Emirates Tel: +971 (0)4 887 0615
Tornatech Pte Ltd
Singapore Tel: +65 6795 7823